## FE D3
Date: |  |  |  | 2011-05-03 00:14 |  |  | Max Amps: | 77
SubMonitor ID:
Company: |  |  |  | Jones Hydro - Altheimer
Event | Accumulated Run Time |  |  | Elapsed Run Time |  |  | Condition | Fault | Motor Voltage |  |  | Motor Amps |  |  | % of Max Amps | % Current Unbalance | Parameter Changed To | Trip Enable Flags and Restart Attempt Enable Flags
| Day | Hour | Minute | Day | Hour | Minute |  |  | L1 | L2 | L3 | L1 | L2 | L3 |  |  |  | Underload | Overload | Unbalance | Overheat | Overvoltage | Undervoltage | False Start
0 | 0d | 0h | 0.1m |  |  |  | Motor Rated Frequency | [7 empty] | 0% | 0% | 60
1 | 0d | 0h | 0.1m |  |  |  | Motor Rated Voltage | [7 empty] | 0% | 0% | 460
2 | 0d | 0h | 0.1m |  |  |  | Motor SFA - hundreds digit | [7 empty] | 0% | 0% | 0
3 | 0d | 0h | 0.1m |  |  |  | Motor SFA - tens digit | [7 empty] | 0% | 0% | 7
4 | 0d | 0h | 0.1m |  |  |  | Motor SFA - ones digit | [7 empty] | 0% | 0% | 7
5 | 0d | 0h | 0.1m |  |  |  | Motor SFA - ones digit | [7 empty] | 0% | 0% | 7
6 | 0d | 0h | 0.1m |  |  |  | Manual Reset |  | 508 | 500 | 500 | 1 | 1 | 1 | 1.299% | 0%
7 | 0d | 0h | 0.1m |  |  |  | Power-up Delay |  | 503 | 497 | 494 | 1 | 1 | 1 | 1.299% | 0%
8 | 0d | 5h | 58.4m | 0d | 5h | 58.3m | Power-up Delay |  | 503 | 496 | 494 | 1 | 1 | 1 | 1.299% | 0%
9 | 0d | 6h | 9.1m | 0d | 0h | 10.7m | Power-up Delay |  | 500 | 494 | 492 | 1 | 1 | 1 | 1.299% | 0%
10 | 0d | 6h | 12.5m | 0d | 0h | 3.4m | Power-up Delay |  | 504 | 498 | 496 | 1 | 1 | 1 | 1.299% | 0%
11 | 0d | 6h | 12.5m |  |  |  | Power-up Delay |  | 502 | 496 | 494 | 1 | 1 | 1 | 1.299% | 0%
12 | 2d | 5h | 17.1m | 1d | 23h | 4.6m | Tripped | Overvolt | 506 | 497 | 498 | 70 | 69 | 65 | 90.91% | 4.412%
13 | 3d | 22h | 38.3m | 1d | 17h | 21.2m | Tripped | Overvolt | 506 | 499 | 499 | 70 | 69 | 65 | 90.91% | 4.412%
14 | 6d | 1h | 12.1m | 2d | 2h | 33.8m | Tripped | Overvolt | 506 | 500 | 499 | 70 | 69 | 66 | 90.91% | 3.415%
15 | 6d | 1h | 55.0m | 0d | 0h | 42.9m | Tripped | Overvolt | 506 | 498 | 497 | 70 | 69 | 65 | 90.91% | 4.412%
16 | 6d | 8h | 9.3m | 0d | 6h | 14.3m | Tripped | Overvolt | 506 | 499 | 497 | 71 | 69 | 65 | 92.21% | 4.878%
17 | 6d | 16h | 7.6m | 0d | 7h | 58.3m | Tripped | Overvolt | 506 | 499 | 498 | 70 | 69 | 65 | 90.91% | 4.412%
18 | 7d | 9h | 31.5m | 0d | 17h | 23.9m | Tripped | Overvolt | 506 | 499 | 499 | 70 | 69 | 65 | 90.91% | 4.412%
19 | 8d | 9h | 22.6m | 0d | 23h | 51.1m | Tripped | Overvolt | 506 | 498 | 498 | 70 | 69 | 65 | 90.91% | 4.412%
20 | 8d | 15h | 55.4m | 0d | 6h | 32.8m | Tripped | Overvolt | 506 | 499 | 500 | 70 | 69 | 65 | 90.91% | 4.412%
21 | 10d | 8h | 39.8m | 1d | 16h | 44.4m | Tripped | Overvolt | 506 | 497 | 497 | 70 | 70 | 65 | 90.91% | 4.878%
22 | 10d | 15h | 8.5m | 0d | 6h | 28.7m | Tripped | Overvolt | 506 | 498 | 498 | 70 | 69 | 65 | 90.91% | 4.412%
23 | 12d | 8h | 20.9m | 1d | 17h | 12.4m | Tripped | Overvolt | 506 | 498 | 499 | 70 | 69 | 65 | 90.91% | 4.412%
24 | 12d | 11h | 6.8m | 0d | 2h | 45.9m | Tripped | Overvolt | 506 | 497 | 498 | 70 | 69 | 65 | 90.91% | 4.412%
25 | 13d | 16h | 47.6m | 1d | 5h | 40.8m | Tripped | Overvolt | 506 | 499 | 499 | 70 | 69 | 66 | 90.91% | 3.415%
26 | 13d | 19h | 49.5m | 0d | 3h | 1.9m | Tripped | Overvolt | 506 | 498 | 498 | 70 | 69 | 65 | 90.91% | 4.412%
27 | 14d | 2h | 7.1m | 0d | 6h | 17.6m | Tripped | Overvolt | 506 | 498 | 497 | 71 | 69 | 65 | 92.21% | 4.878%
28 | 14d | 4h | 3.9m | 0d | 1h | 56.8m | Tripped | Overvolt | 506 | 499 | 497 | 71 | 69 | 65 | 92.21% | 4.878%
29 | 14d | 19h | 18.2m | 0d | 15h | 14.3m | Tripped | Overvolt | 506 | 499 | 497 | 71 | 69 | 65 | 92.21% | 4.878%
30 | 15d | 1h | 24.1m | 0d | 6h | 5.9m | Tripped | Overvolt | 506 | 499 | 498 | 70 | 69 | 65 | 90.91% | 4.412%
31 | 15d | 16h | 19.5m | 0d | 14h | 55.4m | Total Run Time | [7 empty] | 0% | 0%
32 | 15d | 16h | 19.5m |  |  |  | Overvoltage Trip Point | [7 empty] | 0% | 0% | 114
33 | 15d | 16h | 19.5m |  |  |  | Total Run Time | [7 empty] | 0% | 0%
34 | 16d | 6h | 31.8m | 0d | 14h | 12.3m | Tripped | Unbalance | 503 | 494 | 494 | 70 | 69 | 64 | 90.91% | 5.419%
35 | 18d | 8h | 32.2m | 2d | 2h | 0.4m | Tripped | Unbalance | 507 | 501 | 497 | 72 | 68 | 64 | 93.51% | 5.882%
36 | 18d | 8h | 32.3m | 0d | 0h | 0.1m | Tripped | Unbalance | 502 | 496 | 492 | 72 | 69 | 65 | 93.51% | 5.34%
37 | 18d | 8h | 32.3m |  |  |  | Power-up Delay |  | 505 | 497 | 493 | 1 | 1 | 1 | 1.299% | 0%
38 | 18d | 9h | 40.6m | 0d | 1h | 8.3m | Tripped | Unbalance | 499 | 491 | 487 | 71 | 68 | 63 | 92.21% | 6.436%
39 | 18d | 9h | 56.8m | 0d | 0h | 16.2m | Tripped | Unbalance | 506 | 499 | 495 | 72 | 69 | 64 | 93.51% | 6.341%
40 | 18d | 9h | 56.8m |  |  |  | Power-up Delay |  | 508 | 501 | 495 | 1 | 1 | 1 | 1.299% | 0%
41 | 18d | 13h | 45.7m | 0d | 3h | 48.9m | Tripped | Unbalance | 505 | 496 | 493 | 71 | 68 | 64 | 92.21% | 5.419%
42 | 40d | 14h | 2.8m | 22d | 0h | 17.1m | Tripped | Unbalance | 499 | 489 | 490 | 71 | 68 | 63 | 92.21% | 6.436%
43 | 42d | 10h | 52.3m | 1d | 20h | 49.5m | Power-up Delay |  | 493 | 486 | 483 | 1 | 1 | 1 | 1.299% | 0%
44 | 44d | 5h | 1.0m | 1d | 18h | 8.7m | Power-up Delay |  | 500 | 495 | 490 | 1 | 1 | 1 | 1.299% | 0%
45 | 44d | 5h | 1.0m |  |  |  | Power-up Delay |  | 500 | 497 | 489 | 1 | 1 | 1 | 1.299% | 0%
46 | 44d | 5h | 1.0m |  |  |  | Power-up Delay |  | 503 | 498 | 493 | 1 | 1 | 1 | 1.299% | 0%
47 | 44d | 6h | 36.8m | 0d | 1h | 35.8m | Power-up Delay |  | 493 | 491 | 486 | 1 | 1 | 1 | 1.299% | 0%
48 | 44d | 6h | 36.8m |  |  |  | Power-up Delay |  | 498 | 495 | 492 | 1 | 1 | 1 | 1.299% | 0%
49 | 44d | 6h | 36.8m |  |  |  | Power-up Delay |  | 500 | 495 | 493 | 1 | 1 | 1 | 1.299% | 0%
50 | 56d | 7h | 10.6m | 12d | 0h | 33.8m | Power-up Delay |  | 489 | 485 | 486 | 1 | 1 | 1 | 1.299% | 0%
51 | 83d | 13h | 57.2m | 27d | 6h | 46.6m | Power-up Delay |  | 497 | 492 | 492 | 1 | 1 | 1 | 1.299% | 0%
52 | 84d | 1h | 43.0m | 0d | 11h | 45.8m | Power-up Delay |  | 499 | 494 | 494 | 1 | 1 | 1 | 1.299% | 0%
53 | 90d | 16h | 17.4m | 6d | 14h | 34.4m | Power-up Delay |  | 494 | 490 | 485 | 1 | 1 | 1 | 1.299% | 0%
54 | 90d | 16h | 42.8m | 0d | 0h | 25.4m | Power-up Delay |  | 484 | 485 | 479 | 1 | 1 | 1 | 1.299% | 0%
55 | 101d | 10h | 53.2m | 10d | 18h | 10.4m | Power-up Delay |  | 497 | 491 | 492 | 1 | 1 | 1 | 1.299% | 0%
56 | 109d | 8h | 48.4m | 7d | 21h | 55.2m | Tripped | Unbalance | 509 | 499 | 492 | 74 | 69 | 61 | 96.1% | 10.29%
57 | 109d | 9h | 2.0m | 0d | 0h | 13.6m | Tripped | Unbalance | 500 | 497 | 491 | 72 | 67 | 65 | 93.51% | 5.882%
58 | 109d | 9h | 2.0m |  |  |  | Power-up Delay |  | 502 | 497 | 492 | 1 | 1 | 1 | 1.299% | 0%
59 | 109d | 10h | 22.6m | 0d | 1h | 20.6m | Tripped | Unbalance | 501 | 495 | 490 | 71 | 67 | 64 | 92.21% | 5.446%
60 | 109d | 10h | 22.6m |  |  |  | Power-up Delay |  | 503 | 497 | 489 | 1 | 1 | 1 | 1.299% | 0%
61 | 109d | 10h | 25.0m | 0d | 0h | 2.4m | Tripped | Unbalance | 501 | 495 | 490 | 72 | 67 | 64 | 93.51% | 6.404%
62 | 109d | 10h | 25.0m |  |  |  | Power-up Delay |  | 505 | 498 | 491 | 1 | 1 | 1 | 1.299% | 0%
63 | 109d | 10h | 25.0m |  |  |  | Tripped | Unbalance | 502 | 495 | 490 | 72 | 67 | 64 | 93.51% | 6.404%
64 | 109d | 10h | 25.0m |  |  |  | Power-up Delay |  | 505 | 498 | 490 | 1 | 1 | 1 | 1.299% | 0%
65 | 109d | 10h | 25.0m |  |  |  | Power-up Delay |  | 504 | 498 | 490 | 1 | 1 | 1 | 1.299% | 0%
66 | 109d | 10h | 25.0m |  |  |  | Tripped | Unbalance | 502 | 495 | 490 | 72 | 67 | 64 | 93.51% | 6.404%
67 | 109d | 10h | 25.0m |  |  |  | Power-up Delay |  | 505 | 498 | 490 | 1 | 1 | 1 | 1.299% | 0%
68 | 109d | 10h | 25.0m |  |  |  | Tripped | Unbalance | 501 | 496 | 490 | 72 | 67 | 64 | 93.51% | 6.404%
69 | 109d | 10h | 25.0m |  |  |  | Power-up Delay |  | 505 | 499 | 490 | 1 | 1 | 1 | 1.299% | 0%
70 | 109d | 10h | 25.0m |  |  |  | Tripped | Unbalance | 502 | 495 | 489 | 72 | 67 | 64 | 93.51% | 6.404%
71 | 109d | 10h | 25.0m |  |  |  | Power-up Delay |  | 505 | 498 | 490 | 1 | 1 | 1 | 1.299% | 0%
72 | 109d | 10h | 25.0m |  |  |  | Tripped | Unbalance | 502 | 495 | 490 | 72 | 67 | 64 | 93.51% | 6.404%
73 | 109d | 10h | 25.0m |  |  |  | Power-up Delay |  | 505 | 498 | 490 | 1 | 1 | 1 | 1.299% | 0%
74 | 109d | 10h | 25.1m | 0d | 0h | 0.1m | Tripped | Unbalance | 502 | 496 | 490 | 72 | 68 | 63 | 93.51% | 6.897%
75 | 109d | 10h | 25.1m |  |  |  | Power-up Delay |  | 506 | 499 | 491 | 1 | 1 | 1 | 1.299% | 0%
76 | 109d | 10h | 25.1m |  |  |  | Tripped | Unbalance | 503 | 497 | 491 | 73 | 68 | 64 | 94.81% | 6.829%
77 | 109d | 10h | 25.1m |  |  |  | Power-up Delay |  | 506 | 499 | 491 | 1 | 1 | 1 | 1.299% | 0%
78 | 109d | 10h | 25.1m |  |  |  | Tripped | Unbalance | 503 | 497 | 492 | 73 | 68 | 64 | 94.81% | 6.829%
79 | 109d | 10h | 25.1m |  |  |  | Power-up Delay |  | 506 | 500 | 491 | 1 | 1 | 1 | 1.299% | 0%
80 | 109d | 10h | 25.1m |  |  |  | Tripped | Unbalance | 503 | 497 | 490 | 73 | 68 | 64 | 94.81% | 6.829%
81 | 109d | 10h | 25.2m | 0d | 0h | 0.1m | Power-up Delay |  | 506 | 499 | 491 | 1 | 1 | 1 | 1.299% | 0%
82 | 109d | 10h | 25.2m |  |  |  | Tripped | Unbalance | 503 | 496 | 490 | 73 | 68 | 64 | 94.81% | 6.829%
83 | 109d | 10h | 25.2m |  |  |  | Power-up Delay |  | 506 | 500 | 491 | 1 | 1 | 1 | 1.299% | 0%
84 | 109d | 10h | 25.2m |  |  |  | Tripped | Unbalance | 503 | 497 | 492 | 73 | 68 | 64 | 94.81% | 6.829%
85 | 109d | 10h | 25.2m |  |  |  | Power-up Delay |  | 505 | 499 | 491 | 1 | 1 | 1 | 1.299% | 0%
86 | 109d | 10h | 25.2m |  |  |  | Tripped | Unbalance | 499 | 494 | 489 | 72 | 67 | 64 | 93.51% | 6.404%
87 | 109d | 10h | 25.2m |  |  |  | Power-up Delay |  | 505 | 499 | 490 | 1 | 1 | 1 | 1.299% | 0%
88 | 109d | 10h | 25.2m |  |  |  | Tripped | Unbalance | 502 | 496 | 490 | 72 | 67 | 64 | 93.51% | 6.404%
89 | 109d | 10h | 25.2m |  |  |  | Power-up Delay |  | 506 | 499 | 491 | 1 | 1 | 1 | 1.299% | 0%
90 | 109d | 10h | 25.2m |  |  |  | Power-up Delay |  | 507 | 499 | 491 | 1 | 1 | 1 | 1.299% | 0%
91 | 109d | 10h | 25.2m |  |  |  | Tripped | Unbalance | 499 | 493 | 488 | 72 | 68 | 63 | 93.51% | 6.897%
92 | 109d | 10h | 25.2m |  |  |  | Power-up Delay |  | 505 | 499 | 491 | 1 | 1 | 1 | 1.299% | 0%
93 | 109d | 10h | 25.2m |  |  |  | Tripped | Unbalance | 502 | 496 | 490 | 73 | 68 | 64 | 94.81% | 6.829%
94 | 109d | 10h | 25.2m |  |  |  | Power-up Delay |  | 505 | 498 | 490 | 1 | 1 | 1 | 1.299% | 0%
95 | 109d | 10h | 25.2m |  |  |  | Tripped | Unbalance | 503 | 495 | 490 | 72 | 68 | 64 | 93.51% | 5.882%
96 | 109d | 10h | 25.2m |  |  |  | Power-up Delay |  | 505 | 498 | 490 | 1 | 1 | 1 | 1.299% | 0%
97 | 109d | 10h | 25.2m |  |  |  | Tripped | Unbalance | 502 | 496 | 491 | 72 | 68 | 64 | 93.51% | 5.882%
98 | 109d | 10h | 25.2m |  |  |  | Power-up Delay |  | 505 | 498 | 491 | 1 | 1 | 1 | 1.299% | 0%
99 | 109d | 10h | 25.2m |  |  |  | Tripped | Unbalance | 502 | 495 | 490 | 72 | 68 | 64 | 93.51% | 5.882%
100 | 109d | 10h | 25.2m |  |  |  | Power-up Delay |  | 505 | 498 | 490 | 1 | 1 | 1 | 1.299% | 0%
101 | 109d | 10h | 25.2m |  |  |  | Tripped | Unbalance | 502 | 495 | 490 | 72 | 68 | 64 | 93.51% | 5.882%
102 | 109d | 10h | 25.2m |  |  |  | Power-up Delay |  | 505 | 498 | 490 | 1 | 1 | 1 | 1.299% | 0%
103 | 109d | 10h | 25.2m |  |  |  | Tripped | Unbalance | 502 | 497 | 491 | 73 | 68 | 64 | 94.81% | 6.829%
104 | 109d | 10h | 25.7m | 0d | 0h | 0.5m | Tripped | Unbalance | 501 | 495 | 491 | 72 | 68 | 64 | 93.51% | 5.882%
105 | 109d | 10h | 25.7m |  |  |  | Tripped | Unbalance | 503 | 495 | 491 | 72 | 68 | 63 | 93.51% | 6.897%
106 | 109d | 10h | 25.7m |  |  |  | Tripped | Unbalance | 503 | 495 | 490 | 72 | 68 | 64 | 93.51% | 5.882%
107 | 109d | 10h | 25.7m |  |  |  | Power-up Delay |  | 505 | 497 | 490 | 1 | 1 | 1 | 1.299% | 0%
108 | 109d | 10h | 25.7m |  |  |  | Tripped | Unbalance | 502 | 495 | 490 | 72 | 68 | 64 | 93.51% | 5.882%
109 | 109d | 11h | 12.5m | 0d | 0h | 46.8m | Power-up Delay |  | 503 | 497 | 491 | 1 | 1 | 1 | 1.299% | 0%
110 | 109d | 11h | 14.7m | 0d | 0h | 2.2m | Total Run Time | [7 empty] | 0% | 0%
111 | 109d | 11h | 34.5m | 0d | 0h | 19.8m | Total Run Time | [7 empty] | 0% | 0%
112 | 109d | 11h | 40.1m | 0d | 0h | 5.6m | Unbalance Trip Point | [7 empty] | 0% | 0% | 10
113 | 109d | 20h | 38.1m | 0d | 8h | 58.0m | Tripped | Unbalance | 510 | 499 | 489 | 75 | 69 | 60 | 97.4% | 11.76%
114 | 109d | 21h | 4.3m | 0d | 0h | 26.2m | Tripped | Unbalance | 511 | 500 | 490 | 76 | 69 | 61 | 98.7% | 11.17%
115 | 109d | 21h | 5.1m | 0d | 0h | 0.8m | Tripped | Unbalance | 507 | 497 | 487 | 75 | 69 | 61 | 97.4% | 10.73%
116 | 109d | 21h | 5.1m |  |  |  | Tripped | Unbalance | 510 | 498 | 487 | 76 | 70 | 59 | 98.7% | 13.66%
117 | 109d | 21h | 5.1m |  |  |  | Power-up Delay |  | 513 | 501 | 487 | 1 | 1 | 1 | 1.299% | 0%
118 | 109d | 21h | 5.1m |  |  |  | Tripped | Unbalance | 510 | 498 | 486 | 77 | 70 | 60 | 100% | 13.04%
119 | 109d | 21h | 5.1m |  |  |  | Tripped | Unbalance | 513 | 501 | 489 | 77 | 69 | 59 | 100% | 13.66%
120 | 109d | 21h | 5.2m | 0d | 0h | 0.1m | Tripped | Unbalance | 513 | 501 | 489 | 77 | 69 | 59 | 100% | 13.66%
121 | 109d | 21h | 5.2m |  |  |  | Tripped | Unbalance | 509 | 497 | 485 | 76 | 68 | 59 | 98.7% | 12.81%
122 | 109d | 21h | 5.2m |  |  |  | Power-up Delay |  | 515 | 502 | 490 | 1 | 1 | 1 | 1.299% | 0%
123 | 109d | 21h | 5.2m |  |  |  | Tripped | Unbalance | 511 | 500 | 490 | 76 | 70 | 60 | 98.7% | 12.62%
124 | 109d | 21h | 5.2m |  |  |  | Tripped | Unbalance | 512 | 499 | 490 | 75 | 70 | 60 | 97.4% | 12.2%
125 | 109d | 21h | 5.2m |  |  |  | Tripped | Unbalance | 515 | 503 | 493 | 76 | 70 | 60 | 98.7% | 12.62%
126 | 109d | 21h | 5.2m |  |  |  | Tripped | Unbalance | 515 | 502 | 493 | 76 | 70 | 60 | 98.7% | 12.62%
127 | 109d | 21h | 5.2m |  |  |  | Power-up Delay |  | 511 | 498 | 488 | 1 | 1 | 1 | 1.299% | 0%
128 | 109d | 21h | 5.3m | 0d | 0h | 0.1m | Tripped | Unbalance | 510 | 499 | 491 | 75 | 70 | 60 | 97.4% | 12.2%
129 | 109d | 21h | 5.3m |  |  |  | Tripped | Unbalance | 511 | 499 | 491 | 75 | 69 | 60 | 97.4% | 11.76%
130 | 109d | 21h | 5.4m | 0d | 0h | 0.1m | Tripped | Unbalance | 511 | 499 | 491 | 75 | 69 | 60 | 97.4% | 11.76%
131 | 109d | 22h | 3.0m | 0d | 0h | 57.6m | Tripped | Unbalance | 510 | 498 | 490 | 75 | 70 | 61 | 97.4% | 11.17%
132 | 109d | 22h | 14.2m | 0d | 0h | 11.2m | Tripped | Unbalance | 511 | 499 | 490 | 75 | 69 | 60 | 97.4% | 11.76%
133 | 109d | 22h | 14.2m |  |  |  | Power-up Delay |  | 524 | 510 | 493 | 1 | 1 | 1 | 1.299% | 0%
134 | 109d | 22h | 14.2m |  |  |  | Tripped | Unbalance | 520 | 507 | 494 | 79 | 71 | 59 | 102.6% | 15.31%
135 | 109d | 22h | 14.2m |  |  |  | Tripped | Unbalance | 517 | 504 | 491 | 78 | 70 | 59 | 101.3% | 14.49%
136 | 109d | 22h | 14.2m |  |  |  | Tripped | Unbalance | 521 | 508 | 494 | 78 | 71 | 59 | 101.3% | 14.9%
137 | 109d | 22h | 14.2m |  |  |  | Tripped | Unbalance | 522 | 507 | 493 | 79 | 71 | 59 | 102.6% | 15.31%
138 | 109d | 22h | 14.2m |  |  |  | Power-up Delay |  | 527 | 511 | 493 | 1 | 1 | 1 | 1.299% | 0%
139 | 109d | 22h | 14.3m | 0d | 0h | 0.1m | Tripped | Unbalance | 523 | 508 | 494 | 80 | 72 | 58 | 103.9% | 17.14%
140 | 109d | 22h | 14.3m |  |  |  | Power-up Delay |  | 528 | 513 | 495 | 1 | 1 | 1 | 1.299% | 0%
141 | 109d | 22h | 14.3m |  |  |  | Tripped | Overvolt | 524 | 511 | 496 | 80 | 72 | 59 | 103.9% | 16.11%
142 | 109d | 22h | 14.3m |  |  |  | Power-up Delay |  | 529 | 512 | 493 | 1 | 1 | 1 | 1.299% | 0%
143 | 109d | 22h | 14.3m |  |  |  | Power-up Delay |  | 528 | 512 | 494 | 1 | 1 | 1 | 1.299% | 0%
144 | 109d | 22h | 14.3m |  |  |  | Tripped | Overvolt | 525 | 510 | 495 | 81 | 73 | 58 | 105.2% | 17.92%
145 | 109d | 22h | 14.3m |  |  |  | Tripped | Unbalance | 525 | 510 | 495 | 80 | 72 | 58 | 103.9% | 17.14%
146 | 109d | 22h | 14.3m |  |  |  | Tripped | Unbalance | 519 | 506 | 491 | 79 | 70 | 58 | 102.6% | 15.94%
147 | 109d | 22h | 14.3m |  |  |  | Tripped | Unbalance | 526 | 512 | 496 | 80 | 71 | 59 | 103.9% | 15.71%
148 | 109d | 22h | 14.3m |  |  |  | Power-up Delay |  | 510 | 507 | 502 | 1 | 1 | 1 | 1.299% | 0%
149 | 114d | 14h | 54.6m | 4d | 16h | 40.3m | Power-up Delay |  | 495 | 489 | 486 | 1 | 1 | 1 | 1.299% | 0%
150 | 127d | 7h | 14.4m | 12d | 16h | 19.8m | Power-up Delay |  | 495 | 491 | 492 | 1 | 1 | 1 | 1.299% | 0%
151 | 145d | 7h | 49.9m | 18d | 0h | 35.5m | Power-up Delay |  | 484 | 481 | 481 | 1 | 1 | 1 | 1.299% | 0%
152 | 174d | 20h | 31.8m | 29d | 12h | 41.9m | Power-up Delay |  | 480 | 482 | 473 | 1 | 1 | 1 | 1.299% | 0%
153 | 194d | 0h | 20.1m | 19d | 3h | 48.3m | Power-up Delay |  | 497 | 495 | 493 | 1 | 1 | 1 | 1.299% | 0%
154 | 194d | 0h | 20.1m |  |  |  | Power-up Delay |  | 496 | 494 | 492 | 1 | 1 | 1 | 1.299% | 0%
155 | 194d | 0h | 20.2m | 0d | 0h | 0.1m | Power-up Delay |  | 493 | 491 | 489 | 1 | 1 | 1 | 1.299% | 0%
156 | 194d | 0h | 20.2m |  |  |  | Power-up Delay |  | 489 | 488 | 486 | 1 | 1 | 1 | 1.299% | 0%
157 | 194d | 0h | 20.3m | 0d | 0h | 0.1m | Power-up Delay |  | 489 | 487 | 485 | 1 | 1 | 1 | 1.299% | 0%
158 | 194d | 0h | 20.3m |  |  |  | Power-up Delay |  | 490 | 488 | 486 | 1 | 1 | 1 | 1.299% | 0%
159 | 194d | 0h | 20.4m | 0d | 0h | 0.1m | Power-up Delay |  | 475 | 469 | 477 | 126 | 110 | 114 | 163.6% | 8%
160 | 194d | 0h | 20.4m |  |  |  | Tripped | Unbalance | 488 | 484 | 487 | 96 | 54 | 65 | 124.7% | 33.95%
161 | 194d | 0h | 20.5m | 0d | 0h | 0.1m | Tripped | Overload | 474 | 468 | 480 | Overrange |  |  | 0% | 0%
162 | 194d | 0h | 20.5m |  |  |  | Power-up Delay |  | 489 | 487 | 485 | 1 | 1 | 1 | 1.299% | 0%
163 | 194d | 0h | 20.5m |  |  |  | Tripped | Overload | 474 | 468 | 479 | Overrange |  |  | 0% | 0%
164 | 194d | 0h | 20.5m |  |  |  | Power-up Delay |  | 489 | 487 | 485 | 1 | 1 | 1 | 1.299% | 0%
165 | 194d | 0h | 20.5m |  |  |  | Power-up Delay |  | 473 | 466 | 476 | 155 | 133 | 141 | 201.3% | 8.392%
166 | 194d | 0h | 20.5m |  |  |  | Power-up Delay |  | 488 | 486 | 484 | 1 | 1 | 1 | 1.299% | 0%
167 | 194d | 0h | 20.5m |  |  |  | Tripped | Overload | 473 | 466 | 476 | Overrange |  |  | 0% | 0%
168 | 194d | 0h | 20.5m |  |  |  | Power-up Delay |  | 471 | 465 | 475 | 157 | 135 | 144 | 203.9% | 8.028%
169 | 194d | 0h | 20.5m |  |  |  | Power-up Delay |  | 489 | 487 | 485 | 1 | 1 | 1 | 1.299% | 0%
170 | 194d | 0h | 20.5m |  |  |  | Tripped | Overload | 476 | 472 | 481 | Overrange |  |  | 0% | 0%
171 | 194d | 0h | 20.5m |  |  |  | Power-up Delay |  | 491 | 489 | 486 | 1 | 1 | 1 | 1.299% | 0%
172 | 194d | 0h | 20.5m |  |  |  | Power-up Delay |  | 493 | 492 | 490 | 1 | 1 | 1 | 1.299% | 0%
173 | 194d | 0h | 20.5m |  |  |  | Total Run Time | [7 empty] | 0% | 0%
174 | 203d | 13h | 0.4m | 9d | 12h | 39.9m | Tripped | Overload | 487 | 478 | 482 | Overrange |  |  | 0% | 0%
175 | 203d | 13h | 0.4m |  |  |  | Power-up Delay |  | 494 | 491 | 490 | 1 | 1 | 1 | 1.299% | 0%
176 | 203d | 13h | 0.4m |  |  |  | Power-up Delay |  | 493 | 490 | 489 | 1 | 1 | 1 | 1.299% | 0%
177 | 203d | 13h | 0.4m |  |  |  | Power-up Delay |  | 493 | 490 | 489 | 1 | 1 | 1 | 1.299% | 0%
178 | 203d | 13h | 0.4m |  |  |  | Power-up Delay |  | 501 | 498 | 497 | 1 | 1 | 1 | 1.299% | 0%
179 | 204d | 9h | 58.6m | 0d | 20h | 58.2m | Power-up Delay |  | 504 | 501 | 499 | 1 | 1 | 1 | 1.299% | 0%
180 | 235d | 8h | 42.3m | 30d | 22h | 43.7m | Power-up Delay |  | 412 | 411 | 422 | 1 | 1 | 1 | 1.299% | 0%
181 | 238d | 4h | 37.0m | 2d | 19h | 54.7m | Power-up Delay |  | 498 | 493 | 493 | 1 | 1 | 1 | 1.299% | 0%
182 | 238d | 4h | 37.0m |  |  |  | Power-up Delay |  | 497 | 493 | 494 | 1 | 1 | 1 | 1.299% | 0%
183 | 238d | 4h | 37.0m |  |  |  | Power-up Delay |  | 498 | 494 | 495 | 1 | 1 | 1 | 1.299% | 0%
184 | 238d | 4h | 37.0m |  |  |  | Tripped | Overload | 491 | 481 | 494 | Overrange |  |  | 0% | 0%
185 | 238d | 4h | 37.0m |  |  |  | Power-up Delay |  | 499 | 494 | 495 | 1 | 1 | 1 | 1.299% | 0%
186 | 238d | 4h | 37.0m |  |  |  | Power-up Delay |  | 499 | 495 | 496 | 1 | 1 | 1 | 1.299% | 0%
187 | 238d | 4h | 37.0m |  |  |  | Overload Trip Point | [7 empty] | 0% | 0% | 125
188 | 238d | 4h | 37.0m |  |  |  | Overload Trip Point | [7 empty] | 0% | 0% | 125
189 | 238d | 4h | 37.0m |  |  |  | Power-up Delay |  | 500 | 495 | 495 | 1 | 1 | 1 | 1.299% | 0%
190 | 238d | 4h | 37.0m |  |  |  | Timeout for Overvoltage Trip | [7 empty] | 0% | 0% | 1
191 | 238d | 4h | 37.0m |  |  |  | Total Run Time | [7 empty] | 0% | 0%
192 | 238d | 4h | 37.0m |  |  |  | Power-up Delay |  | 500 | 496 | 497 | 1 | 1 | 1 | 1.299% | 0%
193 | 238d | 4h | 37.0m |  |  |  | Total Run Time | [7 empty] | 0% | 0%
194 | 238d | 4h | 37.0m |  |  |  | Total Run Time | [7 empty] | 0% | 0%
195 | 238d | 4h | 37.0m |  |  |  | Total Run Time | [7 empty] | 0% | 0%
196 | 238d | 4h | 37.0m |  |  |  | Total Run Time | [7 empty] | 0% | 0%
197 | 238d | 4h | 37.0m |  |  |  | Total Run Time | [7 empty] | 0% | 0%
198 | 238d | 4h | 37.0m |  |  |  | Total Run Time | [7 empty] | 0% | 0%
199 | 238d | 4h | 37.0m |  |  |  | Total Run Time | [7 empty] | 0% | 0%
200 | 238d | 4h | 37.0m |  |  |  | Switch On |  | 494 | 490 | 491 | 46 | 44 | 43 | 59.74% | 3.759%
201 | 238d | 4h | 37.0m |  |  |  | Tripped | Underload | 494 | 490 | 491 | 48 | 46 | 45 | 62.34% | 3.597%
202 | 238d | 4h | 37.0m |  |  |  | Power-up Delay |  | 496 | 492 | 491 | 1 | 1 | 1 | 1.299% | 0%
203 | 238d | 4h | 37.0m |  |  |  | Switch On |  | 493 | 489 | 490 | 83 | 83 | 80 | 107.8% | 2.439%
204 | 238d | 4h | 37.6m | 0d | 0h | 0.6m | Tripped | Underload | 495 | 490 | 492 | 49 | 48 | 46 | 63.64% | 3.497%
205 | 238d | 4h | 37.6m |  |  |  | Power-up Delay |  | 496 | 492 | 491 | 1 | 1 | 1 | 1.299% | 0%
206 | 238d | 4h | 37.6m |  |  |  | Switch On |  | 493 | 489 | 491 | 82 | 82 | 79 | 106.5% | 2.469%
207 | 238d | 4h | 38.1m | 0d | 0h | 0.5m | Tripped | Underload | 495 | 490 | 492 | 49 | 48 | 47 | 63.64% | 2.083%
208 | 238d | 4h | 38.1m |  |  |  | Switch On |  | 495 | 491 | 492 | 45 | 43 | 43 | 58.44% | 3.053%
209 | 238d | 4h | 38.2m | 0d | 0h | 0.1m | Tripped | Underload | 495 | 491 | 492 | 47 | 45 | 45 | 61.04% | 2.92%
210 | 238d | 4h | 38.2m |  |  |  | Timed Reset |  | 495 | 491 | 493 | 53 | 52 | 50 | 68.83% | 3.226%
211 | 238d | 9h | 52.8m | 0d | 5h | 14.6m | Switch Off |  | 501 | 496 | 497 | 1 | 1 | 1 | 1.299% | 0%
212 | 238d | 9h | 52.8m |  |  |  | Switch On |  | 496 | 491 | 495 | 44 | 44 | 43 | 57.14% | 1.527%
213 | 238d | 9h | 52.9m | 0d | 0h | 0.1m | Tripped | Underload | 496 | 491 | 494 | 47 | 46 | 45 | 61.04% | 2.174%
214 | 238d | 9h | 52.9m |  |  |  | Switch On |  | 494 | 489 | 492 | 44 | 43 | 43 | 57.14% | 1.538%
215 | 238d | 9h | 52.9m |  |  |  | Tripped | Underload | 494 | 490 | 493 | 46 | 46 | 45 | 59.74% | 1.46%
216 | 238d | 9h | 53.0m | 0d | 0h | 0.1m | Switch On |  | 499 | 494 | 498 | 44 | 43 | 43 | 57.14% | 1.538%
217 | 238d | 9h | 53.0m |  |  |  | Tripped | Underload | 499 | 493 | 497 | 46 | 46 | 45 | 59.74% | 1.46%
218 | 238d | 9h | 53.0m |  |  |  | Timed Reset |  | 495 | 490 | 494 | 52 | 52 | 51 | 67.53% | 1.29%
219 | 238d | 10h | 30.3m | 0d | 0h | 37.3m | Switch Off |  | 503 | 497 | 500 | 1 | 1 | 1 | 1.299% | 0%
220 | 238d | 10h | 30.3m |  |  |  | Switch On |  | 496 | 490 | 494 | 44 | 43 | 43 | 57.14% | 1.538%
221 | 238d | 10h | 30.3m |  |  |  | Tripped | Underload | 495 | 491 | 494 | 46 | 46 | 46 | 59.74% | 0%
222 | 238d | 10h | 30.3m |  |  |  | Switch On |  | 495 | 490 | 493 | 44 | 44 | 43 | 57.14% | 1.527%
223 | 238d | 10h | 30.4m | 0d | 0h | 0.1m | Tripped | Underload | 495 | 491 | 494 | 46 | 46 | 45 | 59.74% | 1.46%
224 | 238d | 10h | 30.4m |  |  |  | Manual Reset |  | 498 | 494 | 496 | 1 | 1 | 1 | 1.299% | 0%
225 | 238d | 10h | 30.4m |  |  |  | Motor SFA - tenths digit | [7 empty] | 0% | 0% | 0
226 | 238d | 10h | 30.4m |  |  |  | Motor SFA - tens digit | [7 empty] | 0% | 0% | 6
227 | 238d | 10h | 30.4m |  |  |  | Motor SFA - ones digit | [7 empty] | 0% | 0% | 2
228 | 238d | 10h | 30.4m |  |  |  | Overload Trip Point | [7 empty] | 0% | 0% | 115
229 | 238d | 10h | 30.4m |  |  |  | Underload Trip Point | [7 empty] | 0% | 0% | 75